## Variables
Device | Element | Function | Meaningful values / Range | Other Information | Description
Interlock | C1 | Key |  |  | show key position
| C2 | Door status |  |  | Door open/close
| C2 | Door power |  |  | Magnet lock powered on/off
| C3 | drive interlock state |  |  | Show actual
| C4 | E- relay status |  |  | Show e-relay status
| C5 | E-stop modbus
Lights | C235 | Control room lights new status |  | Changes relay
| C236 | Utilities room lights new status |  | Changes relay
| C237 | Spectrograph room lights new status |  | Changes relay
| C238 | UMA lights new status |  | Changes relay
| C239 | Tel Plat bright lights new status |  | Changes relay
| C240 | Tel plat red new status |  | Changes relay
| C335 | Control room lights status
| C336 | Utilities room lights status
| C337 | Spectrograph room lights status
| C338 | UMA lights status
| C339 | Tel Plat bright lights status
| C340 | Tel plat red status
Shutter movement | C100 | Drive enable
| C101 | Drive state
| C102 | Motor direction
| C103 | Drive brake
| D104-105 | Drive velocity
| C105 | NE limit switch status
| C106 | NW limit switch status
| C107 | SE limit switch status
| C108 | SW limit switch status
| C110 | Overcurrent
| D120 | Open timeout
| D121 | Close timeout
| C122 | Open small move timeout
| D130 | Drive current
| T0 | Timout_error
| D150 | dome Counter
Emergency stop | C200 | E-Stop
| C201 | E-Stop status
| C202 | E-relay reset.
HVAC | D500
D101

## Input
Device | Element | Function | Meaningful values / Range | Other Information | Description
Interlock | X0 | Safety key |  | Engaged?
| X1 | Door status |  | Open/Close
| X2 | Door Power
| X4 | E-Stop
Shows actual driving state
Lights | X10 | Control room lights curr det
| X11 | Utilities room lights curr det
| X12 | Spectrograph room lights curr det
| X13 | UMA lights curr det
| X14 | Tel Plat bright lights curr det
| X15 | Tel plat red curr det
Shutter movement | X9 | NE limit switch
| X10 | NW limit switch
| X11 | SE limit switch
| X12 | SW limit switch
| WX0 | Motor counter

## Output
Device | Element | Function | Meaningful values / Range | Other Information | Description
Interlock | Y0 | Indicator light | Bit
| Y1 | Door magnet | Bit
| Y4 | E-stop
Lights | Y3 | Control room lights relay
| Y4 | Utilities room lights relay
| Y5 | Spectrograph room lights relay
| Y6 | UMA lights relay
| Y7 | Tel Plat bright lights relay
| Y8 | Tel plat red relay
Shutter movement | Y9 | Brake

## Modbus
Device | Element | Function | Read/Write | Meaningful values / Range | Other Information | Description
Interlock | MC1 | Key | R | X0 |  | show key position
| MC2 | Door status | R |  |  | Door open/close
| MC3 | Drive interlock state | R
Show actual status
Lights | MC235 | Control room lights new status | W |  | Changes relay
| MC236 | Utilities room lights new status | W |  | Changes relay
| MC237 | Spectrograph room lights new status | W |  | Changes relay
| MC238 | UMA lights new status | W |  | Changes relay
| MC239 | Tel Plat bright lights new status | W |  | Changes relay
| MC240 | Tel plat red new status | W |  | Changes relay
Roll-off movement | MC100 | Drive enable | W
| MC101 | Motor direction | W | 0 closes / 1 opens.
| MHR510 | User defined drive frequency | W | int decimal (100 = 10 Hz).
| MC102 | Drive state | R
| MC103 | Drive brake | R
| MHR400 | Present Fault Record | R
| MHR401 | Second Most Recent Fault Record | R
| MHR402 | Third Most Recent Fault Record | R
| MHR403 | Fourth Most Recent Fault Record | R
| MHR404 | Fifth Most Recent Fault Record | R
| MHR405 | Sixth Most Recent Fault Record | R
| MHR411 | Status Monitor 1 | R
| MHR412 | Status monitor 2 | R
| MHR413 | Frequency Command | R
| MHR414 | Output Frequency | R
| MHR415 | Output Current | R
| MHR417 | Output Voltage | R
| MHR418 | Motor current RPM | R
| MC105 | NE limit switch status | R
| MC106 | NW limit switch status | R
| MC107 | SE limit switch status | R
| MC108 | SW limit switch status | R
| MHR150 | Dome Counter | R
|  | domve velocity | R
Emergency stop | MC200 | E-Stop | W
| MC201 | E-Stop status | R
| MC202 | E-relay reset. | W
HVAC | MHR500
MHR501
GS3 Status | MHR400 | Present Fault Record | R
| MHR401 | Second Most Recent Fault Record | R
| MHR402 | Third Most Recent Fault Record | R
| MHR403 | Fourth Most Recent Fault Record | R
| MHR404 | Fifth Most Recent Fault Record | R
| MHR405 | Sixth Most Recent Fault Record | R
| MHR406 | Serial Comm (RS-485) Speed Reference | R
| MHR407 | Serial Comm RUN Command | R
| MHR408 | Serial Comm Direction Command | R
| MHR409 | Serial Comm External Fault | R
| MHR410 | Serial Comm Fault Reset | R
| MHR411 | Serial Comm JOG Command | R

## GS3 read
GS3 code | GS3 Var name | Modbus GS3 Var | Do more Var
P6.31 | Present Fault Record | 41568 | MHR400
P6.32 | Second Most Recent Fault Record | 41569 | MHR401
P6.33 | Third Most Recent Fault Record | 41570 | MHR402
P6.34 | Fourth Most Recent Fault Record | 41571 | MHR403
P6.35 | Fifth Most Recent Fault Record | 41572 | MHR404
P6.36 | Sixth Most Recent Fault Record | 41573 | MHR405
P9.26 | Serial Comm (RS-485) Speed Reference | 42331 | MHR410
| Status monitor 1 | 48449 | MHR411
| Status monitor 2 | 48450 | MHR412
| Frequency Command F | 48451 | MHR413
| Output Frequency | 48452 | MHR414
| Output Current A | 48453 | MHR415
git